## How to use
Ohmsight Risk-Based Electrical Review Model
Deficiency taxonomy, evidence-based risk scoring, and code mapping. Version 0.2, September 2026. Author: Ezeoma (Lewis) Igwe.
What this workbook does
1. Taxonomy: 60 recurring electrical design deficiencies in 7 groups (general documentation, PV, energy storage, emergency and standby, fire alarm, service and distribution, load calculations).
2. Risk model: Risk = Severity score x Frequency score (maximum 25). Deficiencies are ranked into a 'review first' order and three priority tiers.
3. Code mapping: each deficiency is linked to NEC 2023 and California Title 24 sections by number only. No code text is reproduced.
How frequency is scored (the evidence method)
Frequency is not guessed. It is scored from published sources listed on the Sources tab:
- AHJ checklists: how many independent jurisdiction or code-body plan review checklists require or flag the item (CA, VA, AZ, WI, and ICC).
- Industry sources: how many plan-set or engineering sources describe the item as a common reason plans are returned.
- Top problem: whether any source names it as the most common or most often overlooked problem.
The rules that turn these counts into a 1 to 5 score are on the Scales tab. The Field adjustment column (-2 to +2) lets the reviewer adjust each score from measured project data, with a note explaining why.
Tabs
Taxonomy and Risk: the main table. Yellow cells are inputs.
Review First: every deficiency in rank order. Updates automatically.
Summary by System: counts, Tier 1 items, and average risk per group. Updates automatically.
Sources: the evidence register with links.
Scales: severity weights, frequency evidence rules, and tier thresholds.
Limits of this version
A. Frequency reflects how often an item appears in published checklists and industry reporting, not a measured rate from reviewed projects. The next version will calibrate it with results from sample projects and pilot jurisdictions using the Field adjustment column.
B. Sources are weighted toward residential PV, where public data is richest. Low scores for items such as EV load or arc energy reduction mean little published evidence, not proof that the problem is rare.
C. Industry articles (S9 to S11) are commercial sources. Their counts are used, but figures they quote without citation (for example, a claimed 30% to 40% rejection share for PV conductor sizing) are not used as numeric inputs.
D. Reference check column: 'Confirmed in source' means a listed source cites the same section for the same requirement. 'Needs check' means a standard section that should still be confirmed against the adopted edition before publication.
E. No agency records were used. All data comes from public documents.
Code editions referenced
NEC 2023 (NFPA 70), the base of the 2025 California Electrical Code (Title 24, Part 3), effective January 1, 2026. Other Title 24 parts: Part 2 CBC, Part 2.5 CRC, Part 6 Energy Code, Part 9 CFC, Part 11 CALGreen. NFPA 72 and NFPA 110 where the electrical code does not set the requirement.
The NEC column is the part of the model that transfers directly to any U.S. jurisdiction that adopts the NEC.

## Taxonomy and Risk
Ohmsight deficiency taxonomy, evidence-based risk model, and code mapping
Yellow = input. Frequency is scored from the published sources on the Sources tab; use Field adjustment only with a note. Code references are section numbers only.
ID | System | Deficiency | What the reviewer checks | Severity category | Severity score | AHJ checklists citing | Industry sources citing | Named as top problem? | Source IDs | Evidence frequency | Field adjustment | Final frequency | Risk score | Priority tier | Rank | NEC 2023 reference | California Title 24 / other reference | Reference check | Notes | Sort key
GD-01 | General documentation | Wrong or outdated code edition cited on plans | Code editions on cover sheet match the editions adopted by the jurisdiction | Administrative | 1 | 0 | 2 | No | S10, S11 | 3 | 0 | 3 | 3 | Tier 3: Spot check | 52 | 90.4 (enforcement) | Title 24 Part 3 CEC 2025 (NEC 2023 base) | Confirmed in source (S14) |  | 313
GD-02 | General documentation | One-line diagram missing required ratings or replaced by a riser diagram | Conductors, OCPDs, disconnects, grounding, AIC and SCCR shown for service and feeders | Administrative | 1 | 3 | 1 | No | S4, S5, S6, S10 | 4 | 0 | 4 | 4 | Tier 3: Spot check | 51 | None (submittal requirement) | Part 2 CBC Ch. 1 construction documents; local submittal rules | Needs check |  | 414
GD-03 | General documentation | Resubmittal response letter does not address each correction | Each correction answered with sheet and detail reference, not 'will comply' | Administrative | 1 | 1 | 0 | No | S4 | 2 | 0 | 2 | 2 | Tier 3: Spot check | 56 | None (process item) | Local plan check procedures | Not a code section |  | 212
PV-01 | PV | Maximum PV DC circuit voltage not calculated with low-temperature correction | String Voc x temperature factor vs. inverter, module, and DC equipment ratings | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 26 | 690.7 | Part 3 CEC: same section | Confirmed in source (S1) |  | 842
PV-02 | PV | PV circuit conductors or overcurrent devices not sized with required continuous-current factors | Isc x 125% x 125%, ampacity after correction and adjustment, OCPD rating | Fire | 4 | 1 | 2 | Yes | S1, S10, S11 | 5 | 0 | 5 | 20 | Tier 1: Review first | 9 | 690.8; 690.9 | Part 3 CEC: same sections | Confirmed in source (S1) |  | 2045
PV-03 | PV | Rapid shutdown not specified or described only in vague notes | Listed rapid shutdown method, initiation device location, array boundary | Life safety | 5 | 1 | 1 | No | S1, S11 | 4 | 0 | 4 | 20 | Tier 1: Review first | 3 | 690.12; 690.56(C) | Part 3 CEC: same sections | Confirmed in source (S1) |  | 2054
PV-04 | PV | Roof access pathways and setbacks for firefighters not shown | Pathway widths, ridge setbacks, array layout on roof plan | Life safety | 5 | 1 | 2 | Yes | S1, S9, S11 | 5 | 0 | 5 | 25 | Tier 1: Review first | 1 | None (building and fire code item) | Part 2 CBC 3111.3.4; Part 2.5 CRC R329.6 | Confirmed in source (S1) |  | 2555
PV-05 | PV | Point of interconnection unclear or load-side connection exceeds busbar limits | Load-side vs. supply-side clearly shown; 705.12(B)(3) option used and calculated | Fire | 4 | 1 | 1 | Yes | S1, S9 | 5 | 0 | 5 | 20 | Tier 1: Review first | 10 | 705.12(B)(3) | Part 3 CEC: same section | Confirmed in source (S1) |  | 2045
PV-06 | PV | Supply-side connection details incomplete | Conductor sizing, OCPD, disconnect, and connection method ahead of service disconnect | Fire | 4 | 0 | 1 | No | S9 | 3 | 0 | 3 | 12 | Tier 2: Standard | 17 | 705.11 | Part 3 CEC: same section | Needs check |  | 1243
PV-07 | PV | PV disconnects not located, grouped, or identified as required | AC and DC disconnect locations, grouping, AC disconnect within sight of inverter | Life safety | 5 | 1 | 0 | No | S1 | 2 | 0 | 2 | 10 | Tier 2: Standard | 18 | 690.13; 690.15; 705.20 | Part 3 CEC: same sections | Confirmed in source (S1) |  | 1052
PV-08 | PV | Required PV labels and power source directory missing | Label schedule and directory showing all power sources and disconnect locations | Administrative | 1 | 1 | 1 | Yes | S1, S9 | 5 | 0 | 5 | 5 | Tier 3: Spot check | 44 | 690.13; 690.53; 690.56; 705.10 | Part 3 CEC: same sections | Confirmed in source (S1) |  | 515
PV-09 | PV | DC arc-fault circuit protection not specified | Listed PV arc-fault protection for DC circuits at 80 V or more | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 27 | 690.11 | Part 3 CEC: same section | Confirmed in source (S1) |  | 842
PV-10 | PV | PV grounding and bonding not detailed | Array and racking bonding (e.g., UL 2703 racking), GEC sizing and connection | Life safety | 5 | 1 | 1 | No | S1, S10 | 4 | 0 | 4 | 20 | Tier 1: Review first | 4 | 690.41; 690.43; 690.47; 250.66 | Part 3 CEC: same sections | Needs check |  | 2054
PV-11 | PV | Wiring methods for exposed or ground-mounted PV conductors not specified | Raceway or enclosure, or fencing with bonding, for accessible conductors | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 28 | 690.31 | Part 3 CEC: same section | Needs check |  | 842
PV-12 | PV | Equipment details mismatched across sheets or cut sheets missing | Inverter and module models, specs, and listings match across SLD, schedules, and cut sheets | Administrative | 1 | 1 | 3 | Yes | S1, S9, S10, S11 | 5 | 0 | 5 | 5 | Tier 3: Spot check | 45 | 110.3(B) | Part 3 CEC: same section | Needs check |  | 515
PV-13 | PV | Energy Code PV sizing requirement not met on new construction | PV capacity and solar access roof area vs. compliance documents | Administrative | 1 | 2 | 0 | No | S1, S2 | 3 | 0 | 3 | 3 | Tier 3: Spot check | 53 | None (energy code item) | Part 6 Energy Code 150.1(c)14 residential; 140.10 nonresidential (verify) | Confirmed in source for 150.1(c)14 (S1, S2) |  | 313
ES-01 | Energy storage | ESS disconnecting means missing or not located as required | Disconnect location, lockability, and emergency shutdown initiation for dwellings | Life safety | 5 | 1 | 0 | No | S1 | 2 | 0 | 2 | 10 | Tier 2: Standard | 19 | 706.15 | Part 3 CEC: same section | Confirmed in source (S1, S12) |  | 1052
ES-02 | Energy storage | ESS installed in a location or quantity not permitted | Non-habitable location, aggregate capacity, separation from openings | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 29 | 706.10 | Part 2.5 CRC R328.4; Part 9 CFC 1207 | Confirmed in source (S1, S16) |  | 842
ES-03 | Energy storage | Physical damage or vehicle impact protection for ESS not shown | Bollards, barriers, or elevation where exposed to vehicles | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 30 | 110.27(B) | Part 2.5 CRC R328 (verify subsection) | Confirmed in source for 110.27(B) (S1) |  | 842
ES-04 | Energy storage | ESS circuit sizing or overcurrent protection incorrect, including conductors passing through walls | Circuit current basis, ampacity, OCPD location where conductors pass through walls or floors | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 31 | 706.30; 706.31(F) | Part 3 CEC: same sections | Confirmed in source for 706.31(F) (S1) |  | 842
ES-05 | Energy storage | ESS or inverter listing not documented | UL 9540 system listing, UL 1973 batteries, UL 1741 SA/SB inverters | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 32 | 706.5 (verify) | Part 2.5 CRC R328.2 | Confirmed in source for R328.2 (S1) |  | 842
ES-06 | Energy storage | Power control system listing or settings not documented | Listed PCS and configured current limits protecting busbars and conductors | Fire | 4 | 1 | 0 | No | S1 | 2 | 0 | 2 | 8 | Tier 2: Standard | 33 | 705.13 | Part 3 CEC: same section | Confirmed in source (S1) |  | 842
ES-07 | Energy storage | Battery storage or battery-ready requirements not shown for new dwellings | BESS provided, or BESS-ready interconnection equipment or raceway, where service exceeds 125 A | Administrative | 1 | 2 | 0 | No | S1, S2 | 3 | 0 | 3 | 3 | Tier 3: Spot check | 54 | None (energy code item) | Part 6 Energy Code 150.0(s) | Confirmed in source (S1, S2) |  | 313
EM-01 | Emergency and standby | Emergency or standby system not classified by article (700, 701, or 702) | Each generator and transfer switch labeled with its NEC article on the one-line | Administrative | 1 | 1 | 0 | No | S4 | 2 | 0 | 2 | 2 | Tier 3: Spot check | 57 | 700; 701; 702 | Part 3 CEC: same articles | Confirmed in source (S4) |  | 212
EM-02 | Emergency and standby | Emergency wiring not kept independent of other wiring | Separate raceways, boxes, and enclosures for emergency circuits | Life safety | 5 | 1 | 0 | No | S4 | 2 | 0 | 2 | 10 | Tier 2: Standard | 20 | 700.10(B) | Part 3 CEC: same section | Confirmed in source (S4) |  | 1052
EM-03 | Emergency and standby | Fire protection of emergency feeders not provided where required | Feeder protection method in qualifying occupancies | Life safety | 5 | 0 | 0 | No | None found | 1 | 0 | 1 | 5 | Tier 3: Spot check | 39 | 700.10(D) | Part 3 CEC: same section | Needs check |  | 551
EM-04 | Emergency and standby | Selective coordination not demonstrated | Coordination study for emergency, legally required, elevator, and health care systems | Life safety | 5 | 1 | 1 | No | S4, S8 | 4 | 0 | 4 | 20 | Tier 1: Review first | 5 | 700.32; 701.32; 620.62; 517.17 | Part 3 CEC: same sections | Confirmed in source (S4, S8) |  | 2054
EM-05 | Emergency and standby | Emergency source capacity not justified for connected loads | Load calculation and source sizing for all connected emergency loads | Life safety | 5 | 1 | 0 | No | S5 | 2 | 0 | 2 | 10 | Tier 2: Standard | 21 | 700.4; 701.4 | Part 3 CEC: same sections; Part 2 CBC 2702 | Needs check |  | 1052
EM-06 | Emergency and standby | Optional standby with automatic transfer sized without a load calculation | Generator capacity vs. calculated load, or listed load management | Equipment | 2 | 1 | 0 | No | S5 | 2 | 0 | 2 | 4 | Tier 3: Spot check | 49 | 702.4(B) | Part 3 CEC: same section | Needs check |  | 422
EM-07 | Emergency and standby | Transfer equipment or generator disconnecting means not shown | Transfer switch listing and arrangement, generator disconnect | Life safety | 5 | 1 | 0 | No | S4 | 2 | 0 | 2 | 10 | Tier 2: Standard | 22 | 700.5; 701.5; 702.5; 445.18 | Part 3 CEC: same sections | Needs check |  | 1052
EM-08 | Emergency and standby | Means of egress illumination coverage or source not shown | Photometrics or compliance form, unit equipment or generator source, duration | Life safety | 5 | 3 | 0 | No | S4, S5, S6 | 4 | 0 | 4 | 20 | Tier 1: Review first | 6 | 700.16 | Part 2 CBC 1008 | Confirmed in source for CBC/IBC 1008 (S5) |  | 2054
EM-09 | Emergency and standby | Emergency shutdown for dwelling generators not shown | Outdoor emergency shutdown initiation for one- and two-family dwelling generators | Life safety | 5 | 0 | 0 | No | None found | 1 | 0 | 1 | 5 | Tier 3: Spot check | 40 | 445.19(C) | Part 3 CEC: same section | Confirmed in source (S13) |  | 551
EM-10 | Emergency and standby | Signs identifying on-site power sources missing | Signs at service equipment for emergency and standby sources | Administrative | 1 | 0 | 0 | No | None found | 1 | 0 | 1 | 1 | Tier 3: Spot check | 58 | 700.7; 701.7; 702.7 | Part 3 CEC: same sections | Needs check |  | 111
EM-11 | Emergency and standby | Emergency equipment not protected from fire, flood, or vandalism | Generator room rating, location, and separation of emergency equipment | Fire | 4 | 1 | 0 | No | S4 | 2 | 0 | 2 | 8 | Tier 2: Standard | 34 | 700.12; 701.12 | Part 2 CBC 2702; NFPA 110 | Confirmed in source (S4) |  | 842
FA-01 | Fire alarm | Secondary power (battery) calculations missing or insufficient | 24-hour standby plus alarm duration, with aging factor | Life safety | 5 | 2 | 0 | No | S3, S7 | 3 | 0 | 3 | 15 | Tier 2: Standard | 14 | None (NFPA 72 item) | NFPA 72 10.6.7; Part 9 CFC 907 | Confirmed in source (S3) |  | 1553
FA-02 | Fire alarm | Notification appliance circuit voltage drop calculations missing | End-of-line voltage using degraded battery voltage vs. appliance range | Life safety | 5 | 2 | 0 | No | S3, S7 | 3 | 0 | 3 | 15 | Tier 2: Standard | 15 | None (NFPA 72 item) | NFPA 72 (NAC); Part 9 CFC 907 | Confirmed in source (S3) |  | 1553
FA-03 | Fire alarm | Fire alarm branch circuit not dedicated, identified, or secured | Dedicated circuit, red marking, lockable disconnect, location identified at panel | Life safety | 5 | 1 | 0 | No | S3 | 2 | 0 | 2 | 10 | Tier 2: Standard | 23 | 760.41; 760.121 | Part 3 CEC: same sections; Part 9 CFC 907 | Confirmed in source (S3) |  | 1052
FA-04 | Fire alarm | Fire alarm cable types or wire sizes not identified | Cable types for plenum and riser spaces; wire gauges on riser diagram | Fire | 4 | 1 | 0 | No | S7 | 2 | 0 | 2 | 8 | Tier 2: Standard | 35 | 760.135; 760.154 | Part 3 CEC: same sections | Needs check |  | 842
FA-05 | Fire alarm | Power-limited fire alarm circuits not separated from power circuits | Separation or barriers from light, power, and Class 1 circuits | Life safety | 5 | 0 | 0 | No | None found | 1 | 0 | 1 | 5 | Tier 3: Spot check | 41 | 760.136 | Part 3 CEC: same section | Needs check |  | 551
FA-06 | Fire alarm | Pathway class or survivability not specified | Pathway class designations and survivability for relocation or partial evacuation | Life safety | 5 | 1 | 0 | No | S3 | 2 | 0 | 2 | 10 | Tier 2: Standard | 24 | 728 (where fire-resistive cable used) | NFPA 72 Ch. 12 (pathway class and survivability) | Confirmed in source for NFPA 72 Ch. 12 (S3) |  | 1052
SD-01 | Service and distribution | Available fault current not shown, or equipment ratings below it | Utility fault current letter, fault calcs to all equipment, AIC and SCCR, field marking | Life safety | 5 | 3 | 2 | Yes | S4, S5, S6, S8, S10 | 5 | 0 | 5 | 25 | Tier 1: Review first | 2 | 110.9; 110.10; 110.24 | Part 3 CEC: same sections | Confirmed in source (S4, S8) |  | 2555
SD-02 | Service and distribution | Working space or dedicated equipment space insufficient | Clearances, dedicated space, obstructions, and egress shown on plans | Life safety | 5 | 3 | 0 | No | S4, S5, S6 | 4 | 0 | 4 | 20 | Tier 1: Review first | 7 | 110.26 | Part 3 CEC: same section | Confirmed in source (S4, S5) |  | 2054
SD-03 | Service and distribution | Panel schedules incomplete or panelboard rating inadequate | Voltage, phase, bus rating, AIC, loads in A or kVA, main protection | Fire | 4 | 3 | 1 | Yes | S4, S5, S6, S10 | 5 | 0 | 5 | 20 | Tier 1: Review first | 11 | 408.36 | Part 3 CEC: same section | Needs check |  | 2045
SD-04 | Service and distribution | Conductor ampacity wrong after correction, adjustment, or terminal limits | Ampacity table, correction and adjustment factors, terminal temperature, OCPD | Fire | 4 | 2 | 1 | Yes | S4, S5, S10 | 5 | 0 | 5 | 20 | Tier 1: Review first | 12 | 310.16; 240.4; 110.14(C) | Part 3 CEC: same sections | Confirmed in source (S5) |  | 2045
SD-05 | Service and distribution | Grounding and bonding details or conductor sizes missing | GEC and EGC sizes, electrodes, bonding, separately derived systems | Life safety | 5 | 3 | 2 | No | S4, S5, S6, S8, S10 | 4 | 0 | 4 | 20 | Tier 1: Review first | 8 | 250.50; 250.52; 250.66; 250.122; 250.30 | Part 3 CEC: same sections | Confirmed in source (S4, S5) |  | 2054
SD-06 | Service and distribution | GFCI or AFCI protection not shown where required | Protected locations and device types on power plans and panel schedules | Life safety | 5 | 2 | 0 | No | S5, S6 | 3 | 0 | 3 | 15 | Tier 2: Standard | 16 | 210.8; 210.12 | Part 3 CEC: same sections | Confirmed in source for 210.8 (S5) |  | 1553
SD-07 | Service and distribution | Ground-fault protection of equipment not provided where required | GFPE on qualifying services and feeders | Fire | 4 | 1 | 0 | No | S5 | 2 | 0 | 2 | 8 | Tier 2: Standard | 36 | 230.95; 215.10 | Part 3 CEC: same sections | Confirmed in source (S5) |  | 842
SD-08 | Service and distribution | Multiple services or building disconnects not permitted or not identified | Number of services and disconnects, grouping, and marking | Life safety | 5 | 1 | 0 | No | S5 | 2 | 0 | 2 | 10 | Tier 2: Standard | 25 | 230.2; 230.70; 230.71; 225.31 | Part 3 CEC: same sections | Confirmed in source (S5) |  | 1052
SD-09 | Service and distribution | Transformer protection or secondary conductor rules not met | Primary and secondary OCPD, secondary conductor length and protection | Fire | 4 | 1 | 0 | No | S6 | 2 | 0 | 2 | 8 | Tier 2: Standard | 37 | 450.3; 240.21(C) | Part 3 CEC: same sections | Needs check |  | 842
SD-10 | Service and distribution | Arc energy reduction not provided for large overcurrent devices | Arc energy reduction method for devices rated 1200 A and above | Life safety | 5 | 0 | 0 | No | None found | 1 | 0 | 1 | 5 | Tier 3: Spot check | 42 | 240.87 | Part 3 CEC: same section | Needs check |  | 551
SD-11 | Service and distribution | Surge protection for dwelling services not shown | Type 1 or Type 2 SPD at dwelling service equipment | Equipment | 2 | 0 | 0 | No | None found | 1 | 0 | 1 | 2 | Tier 3: Spot check | 55 | 230.67 | Part 3 CEC: same section | Needs check |  | 221
SD-12 | Service and distribution | Outdoor emergency disconnect for one- and two-family dwellings not shown | Readily accessible outdoor emergency disconnect and marking | Life safety | 5 | 0 | 0 | No | None found | 1 | 0 | 1 | 5 | Tier 3: Spot check | 43 | 230.85 | Part 3 CEC: same section | Needs check |  | 551
LC-01 | Load calculations | Service or feeder load calculation missing or demand factors not shown | Article 220 method, demand factor breakdown by load type, resulting service size | Fire | 4 | 3 | 1 | Yes | S4, S5, S6, S10 | 5 | 0 | 5 | 20 | Tier 1: Review first | 13 | Article 220; Annex D | Part 3 CEC: same | Confirmed in source (S4) |  | 2045
LC-02 | Load calculations | Existing load not determined correctly for additions or renovations | Existing plus new loads; 12-month demand data or other permitted method | Fire | 4 | 1 | 0 | No | S4 | 2 | 0 | 2 | 8 | Tier 2: Standard | 38 | 220.87 | Part 3 CEC: same section | Confirmed in source (S4) |  | 842
LC-03 | Load calculations | Special loads (sign, track, show window) not included | Sign circuit and load, track lighting and show window loads | Equipment | 2 | 1 | 0 | No | S5 | 2 | 0 | 2 | 4 | Tier 3: Spot check | 50 | 600.5(A); 220.14(F); 220.46 | Part 3 CEC: same sections | Confirmed in source (S5) |  | 422
LC-04 | Load calculations | EV charging load omitted or circuit not sized for continuous load | EVSE load in calculation, dedicated branch circuit, 125% sizing | Fire | 4 | 0 | 0 | No | None found | 1 | 0 | 1 | 4 | Tier 3: Spot check | 46 | 220.57; 625.40; 625.41 | Part 3 CEC: same sections | Needs check |  | 441
LC-05 | Load calculations | Energy management system used to reduce load without listing or settings | Listed EMS, set points, and how they limit load | Fire | 4 | 0 | 0 | No | None found | 1 | 0 | 1 | 4 | Tier 3: Spot check | 47 | 220.70; 750.30; 625.42 | Part 3 CEC: same sections | Needs check |  | 441
LC-06 | Load calculations | Multifamily optional calculation misapplied | Eligibility conditions and demand factors for the optional method | Fire | 4 | 0 | 0 | No | None found | 1 | 0 | 1 | 4 | Tier 3: Spot check | 48 | 220.84 | Part 3 CEC: same section | Needs check |  | 441
LC-07 | Load calculations | EV capable or EV ready requirements not shown | Required EV spaces, raceways, panel capacity, and circuits | Administrative | 1 | 0 | 0 | No | None found | 1 | 0 | 1 | 1 | Tier 3: Spot check | 59 | None (green building code item) | Part 11 CALGreen 4.106.4 (residential, verify); 5.106.5.3 (nonresidential) | Confirmed in source for 5.106.5.3 (S15) |  | 111
LC-08 | Load calculations | Electric-ready requirements (heat pump, cooktop, dryer) not shown | Dedicated circuits, panel space, and labeling for future electric appliances | Administrative | 1 | 0 | 0 | No | None found | 1 | 0 | 1 | 1 | Tier 3: Spot check | 60 | None (energy code item) | Part 6 Energy Code 150.0 electric-ready provisions (verify subsections) | Needs check |  | 111

## Review First
Review-first order
Sorted automatically by risk score; ties broken by severity, then evidence. Change inputs on Taxonomy and Risk, not here.
Rank | ID | System | Deficiency | Severity category | Final frequency | Risk score | Priority tier | NEC 2023 reference | Source IDs
1 | PV-04 | PV | Roof access pathways and setbacks for firefighters not shown | Life safety | 5 | 25 | Tier 1: Review first | None (building and fire code item) | S1, S9, S11
2 | SD-01 | Service and distribution | Available fault current not shown, or equipment ratings below it | Life safety | 5 | 25 | Tier 1: Review first | 110.9; 110.10; 110.24 | S4, S5, S6, S8, S10
3 | PV-03 | PV | Rapid shutdown not specified or described only in vague notes | Life safety | 4 | 20 | Tier 1: Review first | 690.12; 690.56(C) | S1, S11
4 | PV-10 | PV | PV grounding and bonding not detailed | Life safety | 4 | 20 | Tier 1: Review first | 690.41; 690.43; 690.47; 250.66 | S1, S10
5 | EM-04 | Emergency and standby | Selective coordination not demonstrated | Life safety | 4 | 20 | Tier 1: Review first | 700.32; 701.32; 620.62; 517.17 | S4, S8
6 | EM-08 | Emergency and standby | Means of egress illumination coverage or source not shown | Life safety | 4 | 20 | Tier 1: Review first | 700.16 | S4, S5, S6
7 | SD-02 | Service and distribution | Working space or dedicated equipment space insufficient | Life safety | 4 | 20 | Tier 1: Review first | 110.26 | S4, S5, S6
8 | SD-05 | Service and distribution | Grounding and bonding details or conductor sizes missing | Life safety | 4 | 20 | Tier 1: Review first | 250.50; 250.52; 250.66; 250.122; 250.30 | S4, S5, S6, S8, S10
9 | PV-02 | PV | PV circuit conductors or overcurrent devices not sized with required continuous-current factors | Fire | 5 | 20 | Tier 1: Review first | 690.8; 690.9 | S1, S10, S11
10 | PV-05 | PV | Point of interconnection unclear or load-side connection exceeds busbar limits | Fire | 5 | 20 | Tier 1: Review first | 705.12(B)(3) | S1, S9
11 | SD-03 | Service and distribution | Panel schedules incomplete or panelboard rating inadequate | Fire | 5 | 20 | Tier 1: Review first | 408.36 | S4, S5, S6, S10
12 | SD-04 | Service and distribution | Conductor ampacity wrong after correction, adjustment, or terminal limits | Fire | 5 | 20 | Tier 1: Review first | 310.16; 240.4; 110.14(C) | S4, S5, S10
13 | LC-01 | Load calculations | Service or feeder load calculation missing or demand factors not shown | Fire | 5 | 20 | Tier 1: Review first | Article 220; Annex D | S4, S5, S6, S10
14 | FA-01 | Fire alarm | Secondary power (battery) calculations missing or insufficient | Life safety | 3 | 15 | Tier 2: Standard | None (NFPA 72 item) | S3, S7
15 | FA-02 | Fire alarm | Notification appliance circuit voltage drop calculations missing | Life safety | 3 | 15 | Tier 2: Standard | None (NFPA 72 item) | S3, S7
16 | SD-06 | Service and distribution | GFCI or AFCI protection not shown where required | Life safety | 3 | 15 | Tier 2: Standard | 210.8; 210.12 | S5, S6
17 | PV-06 | PV | Supply-side connection details incomplete | Fire | 3 | 12 | Tier 2: Standard | 705.11 | S9
18 | PV-07 | PV | PV disconnects not located, grouped, or identified as required | Life safety | 2 | 10 | Tier 2: Standard | 690.13; 690.15; 705.20 | S1
19 | ES-01 | Energy storage | ESS disconnecting means missing or not located as required | Life safety | 2 | 10 | Tier 2: Standard | 706.15 | S1
20 | EM-02 | Emergency and standby | Emergency wiring not kept independent of other wiring | Life safety | 2 | 10 | Tier 2: Standard | 700.10(B) | S4
21 | EM-05 | Emergency and standby | Emergency source capacity not justified for connected loads | Life safety | 2 | 10 | Tier 2: Standard | 700.4; 701.4 | S5
22 | EM-07 | Emergency and standby | Transfer equipment or generator disconnecting means not shown | Life safety | 2 | 10 | Tier 2: Standard | 700.5; 701.5; 702.5; 445.18 | S4
23 | FA-03 | Fire alarm | Fire alarm branch circuit not dedicated, identified, or secured | Life safety | 2 | 10 | Tier 2: Standard | 760.41; 760.121 | S3
24 | FA-06 | Fire alarm | Pathway class or survivability not specified | Life safety | 2 | 10 | Tier 2: Standard | 728 (where fire-resistive cable used) | S3
25 | SD-08 | Service and distribution | Multiple services or building disconnects not permitted or not identified | Life safety | 2 | 10 | Tier 2: Standard | 230.2; 230.70; 230.71; 225.31 | S5
26 | PV-01 | PV | Maximum PV DC circuit voltage not calculated with low-temperature correction | Fire | 2 | 8 | Tier 2: Standard | 690.7 | S1
27 | PV-09 | PV | DC arc-fault circuit protection not specified | Fire | 2 | 8 | Tier 2: Standard | 690.11 | S1
28 | PV-11 | PV | Wiring methods for exposed or ground-mounted PV conductors not specified | Fire | 2 | 8 | Tier 2: Standard | 690.31 | S1
29 | ES-02 | Energy storage | ESS installed in a location or quantity not permitted | Fire | 2 | 8 | Tier 2: Standard | 706.10 | S1
30 | ES-03 | Energy storage | Physical damage or vehicle impact protection for ESS not shown | Fire | 2 | 8 | Tier 2: Standard | 110.27(B) | S1
31 | ES-04 | Energy storage | ESS circuit sizing or overcurrent protection incorrect, including conductors passing through walls | Fire | 2 | 8 | Tier 2: Standard | 706.30; 706.31(F) | S1
32 | ES-05 | Energy storage | ESS or inverter listing not documented | Fire | 2 | 8 | Tier 2: Standard | 706.5 (verify) | S1
33 | ES-06 | Energy storage | Power control system listing or settings not documented | Fire | 2 | 8 | Tier 2: Standard | 705.13 | S1
34 | EM-11 | Emergency and standby | Emergency equipment not protected from fire, flood, or vandalism | Fire | 2 | 8 | Tier 2: Standard | 700.12; 701.12 | S4
35 | FA-04 | Fire alarm | Fire alarm cable types or wire sizes not identified | Fire | 2 | 8 | Tier 2: Standard | 760.135; 760.154 | S7
36 | SD-07 | Service and distribution | Ground-fault protection of equipment not provided where required | Fire | 2 | 8 | Tier 2: Standard | 230.95; 215.10 | S5
37 | SD-09 | Service and distribution | Transformer protection or secondary conductor rules not met | Fire | 2 | 8 | Tier 2: Standard | 450.3; 240.21(C) | S6
38 | LC-02 | Load calculations | Existing load not determined correctly for additions or renovations | Fire | 2 | 8 | Tier 2: Standard | 220.87 | S4
39 | EM-03 | Emergency and standby | Fire protection of emergency feeders not provided where required | Life safety | 1 | 5 | Tier 3: Spot check | 700.10(D) | None found
40 | EM-09 | Emergency and standby | Emergency shutdown for dwelling generators not shown | Life safety | 1 | 5 | Tier 3: Spot check | 445.19(C) | None found
41 | FA-05 | Fire alarm | Power-limited fire alarm circuits not separated from power circuits | Life safety | 1 | 5 | Tier 3: Spot check | 760.136 | None found
42 | SD-10 | Service and distribution | Arc energy reduction not provided for large overcurrent devices | Life safety | 1 | 5 | Tier 3: Spot check | 240.87 | None found
43 | SD-12 | Service and distribution | Outdoor emergency disconnect for one- and two-family dwellings not shown | Life safety | 1 | 5 | Tier 3: Spot check | 230.85 | None found
44 | PV-08 | PV | Required PV labels and power source directory missing | Administrative | 5 | 5 | Tier 3: Spot check | 690.13; 690.53; 690.56; 705.10 | S1, S9
45 | PV-12 | PV | Equipment details mismatched across sheets or cut sheets missing | Administrative | 5 | 5 | Tier 3: Spot check | 110.3(B) | S1, S9, S10, S11
46 | LC-04 | Load calculations | EV charging load omitted or circuit not sized for continuous load | Fire | 1 | 4 | Tier 3: Spot check | 220.57; 625.40; 625.41 | None found
47 | LC-05 | Load calculations | Energy management system used to reduce load without listing or settings | Fire | 1 | 4 | Tier 3: Spot check | 220.70; 750.30; 625.42 | None found
48 | LC-06 | Load calculations | Multifamily optional calculation misapplied | Fire | 1 | 4 | Tier 3: Spot check | 220.84 | None found
49 | EM-06 | Emergency and standby | Optional standby with automatic transfer sized without a load calculation | Equipment | 2 | 4 | Tier 3: Spot check | 702.4(B) | S5
50 | LC-03 | Load calculations | Special loads (sign, track, show window) not included | Equipment | 2 | 4 | Tier 3: Spot check | 600.5(A); 220.14(F); 220.46 | S5
51 | GD-02 | General documentation | One-line diagram missing required ratings or replaced by a riser diagram | Administrative | 4 | 4 | Tier 3: Spot check | None (submittal requirement) | S4, S5, S6, S10
52 | GD-01 | General documentation | Wrong or outdated code edition cited on plans | Administrative | 3 | 3 | Tier 3: Spot check | 90.4 (enforcement) | S10, S11
53 | PV-13 | PV | Energy Code PV sizing requirement not met on new construction | Administrative | 3 | 3 | Tier 3: Spot check | None (energy code item) | S1, S2
54 | ES-07 | Energy storage | Battery storage or battery-ready requirements not shown for new dwellings | Administrative | 3 | 3 | Tier 3: Spot check | None (energy code item) | S1, S2
55 | SD-11 | Service and distribution | Surge protection for dwelling services not shown | Equipment | 1 | 2 | Tier 3: Spot check | 230.67 | None found
56 | GD-03 | General documentation | Resubmittal response letter does not address each correction | Administrative | 2 | 2 | Tier 3: Spot check | None (process item) | S4
57 | EM-01 | Emergency and standby | Emergency or standby system not classified by article (700, 701, or 702) | Administrative | 2 | 2 | Tier 3: Spot check | 700; 701; 702 | S4
58 | EM-10 | Emergency and standby | Signs identifying on-site power sources missing | Administrative | 1 | 1 | Tier 3: Spot check | 700.7; 701.7; 702.7 | None found
59 | LC-07 | Load calculations | EV capable or EV ready requirements not shown | Administrative | 1 | 1 | Tier 3: Spot check | None (green building code item) | None found
60 | LC-08 | Load calculations | Electric-ready requirements (heat pump, cooktop, dryer) not shown | Administrative | 1 | 1 | Tier 3: Spot check | None (energy code item) | None found

## Summary by System
Summary by system
System | Deficiencies | Tier 1 items | Life-safety items | Average risk score | Highest risk score | References confirmed in source
General documentation | 3 | 0 | 0 | 3 | 4 | 1 of 3
PV | 13 | 5 | 4 | 12.6154 | 25 | 9 of 13
Energy storage | 7 | 0 | 1 | 7.5714 | 10 | 7 of 7
Emergency and standby | 11 | 2 | 7 | 8.6364 | 20 | 6 of 11
Fire alarm | 6 | 0 | 5 | 10.5 | 15 | 4 of 6
Service and distribution | 12 | 5 | 7 | 13.1667 | 25 | 7 of 12
Load calculations | 8 | 1 | 0 | 5.75 | 20 | 4 of 8
All systems | 60 | 13 | 24 | 9.8 | 25 | 38 of 60

## Sources
Evidence register
Public documents only. S1 to S8 count toward AHJ or industry evidence as typed; S12 to S16 were used only to confirm code section numbers.
ID | Title | Publisher | Type | Year | Link | Times cited in model
S1 | Solar PV System Plan Review List (2026 v1.0) | County of Los Angeles Public Works, Building and Safety | AHJ checklist (CA) | 2026 | https://dpw.lacounty.gov/bsd/lib/fp/Building/Solar%20Review/Solar%20PV%20System%20Plan%20Review%20List_2025_v1.0.pdf | 19
S2 | SFD Energy Correction List (2025 v1.0) | County of Los Angeles Public Works, Building and Safety | AHJ checklist (CA) | 2025 | https://pw.lacounty.gov/bsd/lib/fp/Building/Residential/SFD%20Energy%20Correction%20List_2025_V1.0.pdf | 2
S3 | PRC-07F Plan Review Checklist: Fire Alarm Systems | City of Long Beach Development Services | AHJ checklist (CA) | 2026 | https://longbeach.gov/globalassets/lbcd/media-library/documents/formsapplications/plan-review-checklists-prc/prc-07f-plan-review-checklist---fire-alarms-systems | 4
S4 | Electrical Plan Review Requirements (rev. 01-18-2025) | City of Richmond, Virginia | AHJ checklist (VA) | 2025 | https://www.rva.gov/sites/default/files/2025-02/Electrical-Handout_0.pdf | 15
S5 | Electrical Plan Review Checklist | City of Phoenix Planning and Development | AHJ checklist (AZ) | n.d. | https://www.phoenix.gov/content/dam/phoenix/pddsite/documents/trt/external/dsd_trt_pdf_00710.pdf | 14
S6 | Electrical Plan Review Requirements | International Code Council | National code body checklist | n.d. | https://www.iccsafe.org/wp-content/uploads/PR-Elec-Req.pdf | 9
S7 | Fire Alarm Plan Submittal Guidelines | Wisconsin Dept. of Safety and Professional Services | AHJ checklist (WI) | n.d. | https://dsps.wi.gov/Documents/Programs/FireSuppressAlarm/FireAlarmSubmittalGuidelines.pdf | 3
S8 | Electrical Plan Review (application note) | Eaton Bussmann | Industry technical guide | n.d. | https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/technical-literature/bus-ele-an-3015-electrical-plan-review.pdf | 3
S9 | A Guide to PV Plan Sets and Critical Mistakes to Avoid | GreenLancer (plan set provider, 200,000+ projects) | Industry article | n.d. | https://www.greenlancer.com/post/solar-plan-sets | 5
S10 | Why Most Electrical Permit Drawings Get Rejected | MHL Consulting | Industry article | n.d. | https://www.mhlconsulting.co/post/why-most-electrical-permit-drawings-get-rejected-and-how-to-fix-it | 10
S11 | Solar Permit Rejections: 12 Reasons AHJs Send Plans Back | Energyscape Renewables | Industry article | 2026 | https://energyscaperenewables.com/post/solar-permit-rejections-2026/ | 5
S12 | 2023 NEC Updates for Energy Storage Systems | Mayfield Renewables | Code reference | n.d. | https://www.mayfield.energy/technical-articles/2023-nec-updates-for-energy-storage-systems/ | 0
S13 | Emergency Shutdown of Generator Prime Mover | Leviton Captain Code 2023 | Code reference | 2023 | https://captaincode2023.leviton.com/node/349 | 0
S14 | California Electrical Code 2025 (based on NFPA 70, 2023) | UpCodes | Code reference | 2025 | https://up.codes/viewer/california/ca-electric-code-2025 | 0
S15 | 2025 CALGreen 5.106.5.3 Electric vehicle charging | International Code Council | Code reference | 2025 | https://codes.iccsafe.org/s/CAGBC2025P1/chapter-5-nonresidential-mandatory-measures/CAGBC2025P1-Ch05-SubCh5.1-Sec5.106.5.3 | 0
S16 | 706.10 Energy Storage System Locations | UpCodes | Code reference | 2023 | https://up.codes/s/energy-storage-system-locations | 0

## Scales
Scales and settings
Yellow cells are adjustable. All scores reference these cells.
Severity category | Score | Meaning
Life safety | 5 | Failure could injure or kill occupants, workers, or first responders
Fire | 4 | Failure could start or spread a fire or cause major property damage
Equipment | 2 | Failure could damage equipment or cause outages, with limited safety impact
Administrative | 1 | Documentation, labeling, or compliance gap; mainly causes resubmittals
Evidence frequency score | Rule (applied in order) | Plain meaning
5 | Named as a top or most-overlooked problem by a source, and cited by 2 or more sources in total | Widely reported as a leading cause of corrections
4 | Cited by at least 1 industry source and 1 AHJ checklist, or by 3 or more AHJ checklists | Commonly flagged across jurisdictions
3 | Cited by 2 AHJ checklists, or by at least 1 industry source | Regularly flagged
2 | Cited by 1 AHJ checklist | Recognized review item
1 | Code requirement with no published frequency signal found | Not documented as common; calibrate with field data
Priority tier | Minimum risk score | Meaning
Tier 1: Review first | 16 | Check on every submittal before anything else
Tier 2: Standard | 8 | Check on every submittal in normal order
Tier 3: Spot check | 0 | Check when the project type makes it relevant
Final frequency = evidence score + field adjustment, kept between 1 and 5. Life safety is weighted well above administrative items so that a frequent paperwork gap cannot outrank a comparable life-safety gap.